## PAGE 1
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 1 |  | A.C. LINE WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C4XXXX |  | WITH OPTION PE OR PC TO CIRCUIT BREAKER CB1 |  |  |  | OR, WITH OPTION PM TO CIRCUIT BREAKER CB1 |  |  |  | OR, WITH OPTION PD, TO DISCONNECT SWITCH S1
240V | 480V | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | CURRENT RATING (AMPS) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
A004 | B002 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | H_ _36015 | 15 | 14 - 10 OR 8 - 3/0 | 50 OR 120 | H_ _36000S15 | 150 | 14 - 10 OR 8 - 3/0 | 50 OR 120
A006 | B003
B004
B007
A009 | B011 | H_ _36020 | 20 |  |  | H_ _36020 | 20
| B014 | H_ _36025 | 25 |  |  | H_ _36025 | 25
A015 |  | H_ _36030 | 30 |  |  | H_ _36030 | 30
A022 | B021 | H_ _36040 | 40 |  |  | H_ _36040 | 40
A028 | B027 | H_ _36050 | 50 |  |  | H_ _36050 | 50
| B034 | H_ _36060 | 60 |  |  | H_ _36060 | 60
| B040 |  |  |  |  | H_ _36060 | 60
| B052 | H_ _36080 | 80 |  |  | H_ _36080 | 80
A042 |  | H_ _36070 | 70 |  |  | H_ _36070 | 70
| B065 | H_ _36090 | 90 |  |  | H_ _36090 | 90
A054 | B077 | H_ _36100 | 100 |  |  | H_ _36100 | 100
A068 | B096 | H_ _36125 | 125 |  |  | H_ _36125 | 125
A080 |  | H_ _36100 | 100 |  |  | H_ _36100 | 100
A104 |  | H_ _36150 | 150 |  |  | H_ _36150 | 150
| B124 | J_ _36175 | 175 | 4 - 4/0 | 225 | J_ _36175 | 175 | 4 - 4/0 | 225 | J_ _36000S17 | 175 | 4 - 4/0 | 225
A130 |  | J_ _36200LY | 200 |  |  | J_ _36200LY | 200 |  |  | J_ _36000S25LY | 250
A154 | B156 | J_ _36225 | 225 | 3/0 - 350 kcmil | 225 | J_ _36225 | 225 | 3/0 - 350 kcmil | 225 | J_ _36000S25 | 250 | 3/0 - 350 | 225
| B180 | J_ _36250 | 250 |  |  | J_ _36250 | 250
A192 |  | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442 | L_ _36400U31X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442 | L_ _36000S40X | 400 | (1-2) x (2/0 - 500 kcmil) | (1-2) x 442
B240
A248 | B302
A312
A360 |  | M_ _ 36500 | 500 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | M_ _36500 | 500 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450 | L_ _36000S60X | 600
| B361 |  |  |  |  | P_ _ 34060 | 600
| B414 | M_ _ 36600 | 600
| B477 | P_ _ 36080 | 800 |  |  | P_ _ 34080 | 800 |  |  | P_ _34000S80 | 800 | (1-3) x (3/0 - 500 kcmil) | (1-3) x 450
B515
B590
TABLE 2 |  | A.C. LINE WIRING | [6 empty] | TABLE 3 |  | BLOWER MOTOR STARTER WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C4XXXX |  | OR, WITHOUT OPTIONS PE, PC, PM OR PD TO INPUT POWER TERMINAL BLOCK TB2 | [6 empty] | GA800 CONFIGURED MODEL NO. BASE NUMBER G8C4XXXX |  | WITH OPTION TB, TO OVERLOAD RELAY S10
240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) |  |  |  |  | 240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
A004 | B002 | 6H12-TSCU-F | 16 - 10 OR 8 OR 6 - 4 | 35 OR 40 OR 45 |  |  |  |  | A004 | B515 | LRD15 | 18 - 8 | 15
A006 | B003 | [7 empty] | A006 | B590
A009 | B004 | [7 empty] | A009
A015 | B007 | [7 empty] | A015
A022 | B011 | [7 empty] | A022
A028 | B014 | [7 empty] | A028
| B021 | [7 empty] | A042
| B027 | [7 empty] | A054
| B034 | [7 empty] | A068
A080
A042 | B040 | 1423572 | 14 - 10 OR 8 OR 6 - 2/0 | 35 OR 40 OR 120 |  |  |  |  | A104
A054 | B052 | [7 empty] | A130
A068 | B065 | [7 empty] | A154
A080 | B077 | [7 empty] | A192
| B096 | [7 empty] | A248
A104 | B124 | MPDB67003 | 6 - 350 kcmil | 275 |  |  |  |  | A312
A130 | B156 | [7 empty] | A360
A154 | B180 | [8 empty] | B002 | LRD06 | 18 - 8 | 15
A192 | [9 empty] | B003
A248 | B240 | MPDB69123 | (1-2) x (6 - 350 kcmil) | (1-2) x 275 | [5 empty] | B004
A312 | B302 | [8 empty] | B007
A360 | B361 | [8 empty] | B011
| B414 | [8 empty] | B014
| B477 | MPDB69313 | (1-2) x (4 - 500 kcmil) | (1-2) x 500 | [5 empty] | B021
| B515 | [8 empty] | B027
| B590 | 1453411 | (1-2) x (4 - 600 kcmil) | (1-2) x 500 | [5 empty] | B034
B040
B052
B065
B077
B096
B124
B156
B180
B240
B302
B361
B414
B477
EDIT THE REVISION TABLE DATA HERE!!! IT WILL UPDATE THE DRAWING TABLE
[14 empty] | Rev | Description | ECO# | Drawn By | Date
[14 empty] | 01 | ADDED OPTION TB | 10925 | KAP | 2020-10-28
[14 empty] | 00 | INITIAL RELEASE | - | KM | 2018-08-01
ECO #
DRAWN BY
DATE
DESCRIPTION
ADDED OPTION TB
INITIAL RELEASE
REV.
01
00
10925
-
KAP
KM
10/28/20
8/1/18
REVISIONS
TITLE:
CUSTOMER CONNECTION
GA800 CONFIGURED
TYPE 1 HD RATING
SIZE:
C
PAGE:
1 of 2
REVISION:
01
DRAWING #:
UDE00575
DRAWN BY:
K. MALUSIC
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
K. MALUSIC
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
8/1/18
DATE:
8/1/18
DATE:
DATE:
8/1/18
DATE:
8/1/18

## PAGE 2
CUSTOMER WIRING REQUIREMENTS
• FOR 0 TO 100 AMPS, USE A MINIMUM OF 60° - 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
• FOR ABOVE 100 AMPS, USE A MINIMUM OF 75° C COPPER WIRE. (USE COPPER CONDUCTORS ONLY)
TABLE 4 |  | A.C. MOTOR WIRING | [6 empty] | EARTH GROUND WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C4XXXX |  | WITH OPTION PH, TO LOAD REACTOR L4 |  |  | OR, WITH OPTION PH TO TERMINAL BLOCK TB3 |  |  | OR, WITHOUT OPTION PH, TO STANDARD AC DRIVE | GROUND LUG |  | BLOWER MOTOR GROUND LUG
240V | 480V | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | MFG. PART NUMBER | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) |  | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
| B002 | RLW-03P40_ | 22 - 10 | 4.5 |  |  |  | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL USE 75° C COPPER WIRE ONLY | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50 | 14 - 10 OR 8 OR 6 - 4 OR 2 | 35 OR 40 OR 45 OR 50
| B003 | RLW-04P80_
A004 | B004 | RLW-07P60_
| B007 | RLW-00110_
A006 | B011 | RLW-00140_
A009 | B014 | RLW-00210_ | 14 - 6 | 16
A015 |  | RLW-00280_
A022
A028 | B021 | RLW-00350_
| B027 | RLW-00350_
| B034 | RLW-00460_
A042 | B040 | RLW-00550_ | 6 - 4 OR 2 - 1/0 | 45 OR 50
A054 |  | RLW-00830_
A068 |  | RLW-01040_
| B052 |  |  |  | MPDB67003 | 6 - 350 kcmil | 275
B065
A080 | B077
A104 | B096
A130 | B124
A154
| B156 | RLW-02000_ | 2 - 1 OR 1/0 - 2/0 OR 3/0 - 4/0 | 150 OR 180 OR 250 |  |  |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, USE 75° C COPPER WIRE ONLY | 14 - 2/0 | 120
A192 | B180 | RLW-02500_ | 2/0 OR 3/0 - 4/0 OR 250 - 350 OR 400 - 500 | 180 OR 250 OR 325 OR 375
| B240 | RLW-03220_
A248 |  | RLW-03220_ | (1-2) x (6 - 350 kcmil) | (1-2) x 375
A312 | B302 | RLW-04140_
A360 | B361 | RLW-05150_ | [6 empty] | 6 - 250 | 275
| B414 | RLW-06000_ | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR
B477
| B515 | RLW-07500_
B590
TABLE 5 |  | OPTION PL |  |  |  | CONTROL WIRING
GA800 CONFIGURED MODEL NO. BASE NUMBER G8C4XXXX |  | TO DRIVE A1 |  | OR, TO CDBR A2, A3, A4 |  | TERMINAL BLOCK TB1
240V | 480V | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.) | WIRE SIZE RANGE (AWG) | TIGHTENING TORQUE (LB.-IN.)
A004 | B002 | CUSTOMER TO WIRE PER THE AC DRIVE TECHNICAL MANUAL USE 75° C COPPER WIRE ONLY |  |  |  | 26 - 10 | 5.3 - 7.1
A006 | B003
A009 | B004
A015 | B007
A022 | B011
A028 | B014
A042 | B021
A054 | B027
A068 | B034
A080 | B040
A104 | B052
B065
B077
B096
B124
A130 | B156 |  |  | CUSTOMER TO SUPPLY A UL LISTED CLOSED-LOOP CONNECTOR, PER THE CDBR INSTALLATION MANUAL USE 75° C COPPER WIRE ONLY
A154 | B180
A192 | B240
A248 | B302
A312 | B361
A360 | B414
B477
B515
B590
TITLE:
CUSTOMER CONNECTION
GA800 CONFIGURED
TYPE 1 HD RATING
SIZE:
C
PAGE:
2 of 2
REVISION:
01
DRAWING #:
UDE00575
DRAWN BY:
K. MALUSIC
CHECKED:
N. LAWS
TECH:
APPROVED:
K. FLIERL
ORIGINAL DESIGN:
K. MALUSIC
THIS DOCUMENT AND INFORMATION CONTAINED IN IT ARE CONFIDENTIAL, AND CANNOT BE COPIED OR DISCLOSED IN WHOLE OR IN PART WITHOUT THE EXPRESS WRITTEN CONSENT OF YASKAWA AMERICA INC.
DATE:
8/1/18
DATE:
8/1/18
DATE:
DATE:
8/1/18
DATE:
8/1/18